#### Fire Safety Plan

Type Business/Building Name here

Type Building/Business Address here

| Prepared by: | Name of person preparing the Plan | Approved by: |  |
| --- | --- | --- | --- |
|  | Title of person preparing plan |  | Chief Fire Official |
|  | (Title) |  |  |
|  | (Signature) |  | (Signature) |
|  | (Date Prepared) |  | (Date Approved) |

The reproduction or use of this fire safety plan for non-commercial purposes is permitted and encouraged. Permission to reproduce the plan for commercial purposes must be obtained from the Otonabee-South Monaghan Department of Fire and Emergency Services.

| Table of Contents |  |
| --- | --- |
| Title | Page |
| Introduction | 3 |
| Audit of Building Resources | 5 |
| Audit of Human Resources | 9 |
| Supervisory Staff – Appointment and Organization | 10 |
| Training – Supervisory Staff | 12 |
| Emergency Procedures for Occupants | 14 |
| Emergency Procedures for Supervisory Staff | 15 |
| Control of Fire Hazards | 17 |
| Extinguishment and Containing a Fire (extinguisher use) | 22 |
| Alternative Measures | 23 |
| Fire Drills | 29 |
| Maintenance Requirements | 31 |
| Building Schematics | 51 |

Introduction

This fire safety plan is required by the Ontario Fire Code, O. Reg. 213/07, as amended, Div. B Section 2.8.1.

A fire safety plan is designed to provide occupant safety in the event of a fire, to provide effective utilization of the fire safety features of the building and to minimize the possibility of fires, and aid in the protection of occupants in the event of fire. This plan discusses what occupants are required to do in the event of a fire, fire safety, supervisory staff and related duties, and other responsibilities required of specific people related to this building. This fire safety plan should be designed to suit the resources of a specific building or complex of buildings.

In order for this plan to be effective, the owner of the building, management officials and assigned substitutes in positions of authority must know the fire safety plan and be able to implement it in the event of a fire. The Fire Code requires the owner to be responsible for carrying out the provisions for fire safety.

“Owner” is defined as, “any person, firm or corporation having control over any portion of the building or property under consideration and includes the persons in the building or property.”

The Fire Protection and Prevention Act Part VII, Section 28, states that in the case of an offence for contravention of the fire code, a corporation is liable to a fine of not more than $100,000 and an individual is liable to a fine of not more than $50,000 or imprisonment for a term of not more than one year or both.

The Ontario Fire Code, O. Reg. 213/07, as amended, Div. B Sentence 2.8.1.1.(     ), requires the implementation of a Fire Safety Plan for this building/occupancy.  The plan is to be kept in the building in a location approved by the Chief Fire Official.

The fire safety plan approved location is      .

This official document is to be kept readily available at all times for use by staff and fire officials in the event of an emergency.

Updating and Approval:

It is the responsibility of the “owner” to ensure that the information contained within the Fire Safety Plan is accurate and complete, and that the plan is reviewed as required. Ontario Fire Code, O. Reg. 213/07, as amended, Div. B Sentence 2.8.2.1.(4), requires, “the fire safety plan” to “be review as often as necessary, but at intervals not greater than 12 months, to ensure that it takes account of changes in the use and other characteristics of the building.”

A statement of review shall be provided to the Fire Prevention Division of the Otonabee-South Monaghan Department of Fire and Emergency Services on an annual basis, if no changes are required.

The Otonabee-South Monaghan Department of Fire and Emergency Services may require this plan, or parts of it, once approved, to be revised in the event of changes to occupancy or use, changes in the Ontario Fire Code or relevant standards, if the fire safety plan has not been kept current, or because the Chief Fire Official deems the current plan is no longer acceptable.

When the plan is amended in anyway, the Chief Fire Official shall be notified of subsequent changes in the approved fire safety plan.

Submission Procedures:

At least two (2) copies of the Plan (8 ½ X 11 format) must be submitted to the Chief Fire Official.  Upon approval, one copy will be returned to the author and one copy will be retained by the Fire Department.

Audit of Building Resources

| Building/Business Name: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Occupant Load: (if applicable) |  |  |  | Occupancy Type: Assembly Residential Institutional Industrial Mercantile |  |  |  |  |  |  |  |  |  |
| Non-fixed chairs # Chairs with Tables (non-fixed) # Bleachers (SEATING) # Standing: # OCCUPANT LOAD SIGNS MUST BE POSTED. This is the number of occupants legally allowed in an area. See – Occupant Load Information attached. Appendices 1 Page 62 and 63 Fire Prevention must be contacted to ensure occupant load and exits meet all requirements of the Code. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lock Box: Location: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Owner’s Name: Owner’s Address: |  |  |  |  |  |  |  |  |  |  | Phone #: |  |  |
| Date of Construction: Date(s) of Additions: Portables: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Floors: |  | Units/ Floor: Total Units: |  |  |  |  | Total Floors: (including basement) |  | Bldg. Length: |  |  | Width: |  |
| Bldg. Construction: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Roof Construction: |  |  |  |  |  |  |  |  |  |  |  |  |  |

Access:

| Designated Fire Route: No Yes |  |  |  |  |  | Fire Route Signs Posted: No Yes |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Emergency Entry Location: |  |  |  |  | #1: |  |  |  |
| #2: |  |  |  |  |  |  | #3: |  |
| Other Exit Locations: |  |  |  |  |  |  |  |  |
| Property Mgmt.: |  |  |  |  |  |  |  | Phone # |
| Building Superintendent: |  |  |  |  |  |  |  | Phone # |
| Other Call person: |  |  |  |  |  |  |  | Phone # |
| Other Call person: |  |  |  |  |  |  |  | Phone # |
| Access Code: |  |  |  |  |  |  |  |  |
| Hazardous Materials info.: |  |  |  | Locations, material and quantities listing: MSDS Location: |  |  |  |  |

Water:

| Hydrant: Private Other Location: #1 #2 Main size: | Fire Pump: Location: Description: |
| --- | --- |
| Standpipe: Fire Dept. Connection: Shut off Location: |  |
| Sprinkler: Locations: Sprinkler Connected to the Fire Alarm System: No Yes |  |
| Sprinkler Shut Off: Location: |  |
| Hose Cabinets: 1st Floor location: |  |
| 2nd Floor location: |  |
| Below Ground location: |  |

Building Features:

| Annunciator Panel Location: |  |  |  |  | F.F Handset: |  |  |  |  |  | Emergency Voice Communication: |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Electromagnetic Locking Devices: |  |  | No Yes (manual release switch location) |  |  |  |  |  |  |  |  |
| Stairwell #1 | Pressurized: location: |  |  |  |  |  |  |  |  |  |  |
| Stairwell #2 | Pressurized: location: |  |  |  |  |  |  |  |  |  |  |
| Stairwell Door Lock: |  |  |  |  |  |  | Smoke Hatch: |  |  |  |  |
| Smoke Hatch Location: |  |  |  |  |  |  |  | Secured by: |  |  |  |
| FF Elevator: Red or Yellow Helmet Reset location: |  |  |  |  |  |  |  |  | Procedures for use of elevators (see FSP page # ) |  |  |
| Fire Alarm System: |  |  |  |  |  |  |  |  |  |  |  |
| Type: |  |  |  |  |  |  |  |  |  | Monitored: |  |
| Make: |  | Model: |  |  |  | Main Panel Location: |  |  |  |  |  |
| Alarm Company Name: |  |  |  |  |  |  |  |  |  |  | Phone #: |
| Other Special Considerations: |  |  |  |  |  |  |  |  |  |  |  |
| Emergency Lighting: Battery Generator Time allotment: Location of Lights: Exit Signage: No Yes Location(s) throughout building: Emergency Power: Battery Generator Not Applicable Type of generator: Location of generator: Fuel supply location: Transfer switch location: Generator provides power to the following areas/equipment in the building: |  |  |  |  |  |  |  |  |  |  |  |
| Portable Fire Extinguishers: (refer to schematic drawings) |  |  |  |  |  |  |  |  |  |  |  |
| Quantity: |  | Type: |  | Location/Area Protecting: |  |  |  |  |  |  |  |

Utilities and Service Room Locations:

| Heating: | Natural Gas Electric Other |  |  |
| --- | --- | --- | --- |
| Gas Shutoff: |  | HVAC: |  |
| Garbage: |  | Boiler /Furnace: |  |
| Alarm Panel: |  | Laundry: |  |
| Electrical: |  | Mechanical: |  |
| Locker/ Storage: |  | Workshop: |  |
| Domestic Water Shut-off: |  |  |  |

Fixed Extinguishing System for Commercial Cooking Equipment:

| Type: |  |  |
| --- | --- | --- |
| Connected to Fire Alarm System: |  |  |
| Ecology Unit: |  | Protected by Fixed System: |
| Fuel Source: | If “other”, specify: |  |
| Location of fuel shut-off for appliances: |  |  |
| 40BC Extinguisher: | Location: |  |
| K Type (wet) Extinguisher: | Location: |  |

Special Considerations Interior:

Special Considerations Exterior:

Additional Information

For any additional information not already covered:

Audit of Human Resources

All people described below are considered “Supervisory Staff” for the purposes of carrying out specified duties within this fire safety plan and shall be available, upon notification, to carry out said duties as described within this plan.

The Ontario Fire Code definition of “Supervisory Staff”, means those occupants of a building who have some delegated responsibility for the fire safety of other occupants under the fire safety plan and may include the fire department, where the fire department agrees to accept those responsibilities.”

| Business/Building Name: |  |  |  |
| --- | --- | --- | --- |
| Address: |  | Business Phone No.: |  |
| Business Owner’s Name: |  | Phone Number(s): |  |
| Address: |  |  |  |
| Building Owner’s Name: |  | Phone Number(s): |  |
| Address: |  |  |  |
| Manager(s)/Supervisor(s): |  |  |  |
| Name: | Position: |  | Ph. No.: |
| Address: |  |  |  |
| Name: | Position: |  | Ph. No.: |
| Address: |  |  |  |
| Name: | Position: |  | Ph. No.: |
| Address: |  |  |  |
| Name: | Position: |  | Ph. No.: |
| Address: |  |  |  |

Supervisory Staff - Appointment and Organization

The Ontario Fire Code, O. Reg. 213/07, as amended, Div. B Sentence 2.8.2.1.(1)(b), requires “the appointment and organization of designated supervisory staff to carry out fire safety duties”.

The following "Assigned Responsibilities" are suggestions for some responsibilities that need to be assigned to specific people. The "Housekeeping Duties" assigned duties are also some suggstions and all should be discussed and looked at from your buildings perspective. Please indicate actual names and positions of the supervisory staff assigned to the tasks listed, and add/delete tasks as necessary.

| Assigned Responsibilities | Responsibility assigned to: (Name and Position) |
| --- | --- |
| Be in complete charge of the fire safety plan and be aware of the specific responsibilities of the personnel involved. |  |
| Review of Fire Safety Plan (minimum – once every 12 months), and ensure a log is kept of the review. |  |
| Ensure that the information in the fire safety plan is current. |  |
| Ensure any changes to the fire safety plan are forwarded to the attention of the Chief Fire Official at the Otonabee-South Monaghan Department of Fire and Emergency Services. |  |
| Implementation of the fire safety plan. |  |
| Establish and Implement emergency procedures to be followed at the time of an emergency. |  |
| Ensure a copy of the emergency procedures are located and maintained on each floor. |  |
| Appointment and organization of designated supervisory staff that will carry out fire safety duties. |  |
| Assign and train adequate assistance to act in the position of a supervisory staff member when that member is not able to fulfill their duties. |  |
| Instruction and training of supervisory staff to ensure that they are aware of their responsibilities for fire safety and are capable of carrying them out efficiently. |  |
| Ensure that all Occupants are instructed, trained and aware of their responsibilities for fire safety and are capable of carrying them out efficiently. |  |
| Ensure that steps are in place to control fire hazards within the building. |  |
| Ensure Fire Drills are conducted as required, incorporating emergency procedures as appropriate to the building. |  |
| Ensure that the fire drill procedures are prepared in consultation with the Chief Fire Official |  |
| Ensure that the checks, tests and inspections are being completed as required by the Ontario Fire Code, on schedule. |  |

| Assigned Responsibilities | Responsibility assigned to: (Name and Position) |
| --- | --- |
| Ensure that a record of all checks, tests and inspections are completed as required by the Ontario Fire Code. |  |
| Keep a record of all test and corrective measures for a period of at least two (2) years. |  |
| Ensure that there are provisions for alternative measures, for the safety of all occupants, in the event of a shut-down of fire protection equipment. |  |
| Ensure that the maintenance of building facilities is provided for the safety of the occupants. |  |
| Ensure a copy of the schematics are located and maintained on each floor. |  |
| Ensure that the building meets all Ontario Fire Code requirements. |  |
| Ensure Ontario Fire Code violations are corrected forthwith. |  |
| Assigned Responsibilities for all Supervisory Staff (“Housekeeping Duties”) | Responsibility assigned to: (Name and Position) |
| Keep the doors in fire separations closed at all times. |  |
| Keep access to exits and all exits, inside and outside, clear of any obstructions - at all times. |  |
| Keep stairs clear. |  |
| Keep access roadways, fire routes and fire department connections clear and accessible for fire department use. |  |
| Do not permit combustibles to accumulate in quantities or locations that would constitute a fire hazard. |  |
| Promptly remove all combustible waste from areas where waste is placed for disposal, if applicable. |  |
| Maintain the fire protection equipment in good operating condition at all times. |  |
| Participate in fire drills. Occupant participation should be encouraged. |  |
| Have working knowledge of the building fire and life safety equipment. |  |
| Ensure that the building fire and life safety systems are in operating condition, and immediately report/have repaired any issues. |  |
| Arrange for a substitute supervisory staff in your absence. |  |
| In the event of any shut-down of fire and life safety systems, notify the Otonabee-South Monaghan Department of Fire and Emergency Services and initiate alternative measures. |  |
| Comply with the Ontario Fire Code requirements. |  |

Training of Supervisory Staff

Supervisory Staff are to be appointed, organized and trained in their responsibilities for fire safety. If request, all supervisory staff shall be provided with a copy of this fire safety plan to aid them in becoming familiar with the contents and their responsibilities within the plan. (Ontario Fire Code, O. Reg. 213/07, as amended, Div. B Sentence 2.8.2.1.(1)(b)(c)).

Before being given any responsibilities, all Supervisory Staff members shall receive sufficient training in their delegated areas of responsibility. Each Supervisory Staff member shall fully understand all of their responsibilities and shall feel comfortable and confident with these responsibilities.

Emergency procedures must form a part of the training program.  It is presumed that such training will include specific assigned responsibilities as well as certain basic items such as:

- Importance of prompt reporting of fire immediately to the fire department.

- Location and operation of the fire protection equipment installed (such as fire alarm system, manual pull stations, sprinkler system, special extinguishing systems, and fire extinguishers as well as location of main electrical, gas and water shut off valves and location of fire department connections and fire hydrants.

- Importance of limiting and controlling fire and smoke spread.

- Importance of remaining calm.

- Importance of evacuating all persons from building calmly and quickly.

- Any other building specific requirements for knowledge to maintain life safety of supervisors and occupants and cover all requirements of assigned responsibilities.

It is important that all of the supervisory staff team and other staff members survey the building to determine the number and locations of exits.  They must be informed of fire hazards.  They must know occupant emergency procedures as well as their own specific duties and responsibilities.

All members of the supervisory staff team must know how to call the monitoring station (if so equipped) and know the information to relay or ask.  They must take note of the contact person and time the call was made.

All persons of the supervisory staff team must know how to reset the fire alarm system (if so equipped). No person shall reset the fire alarm system without the consent of a Fire Department Official.

Designated supervisory staff team members must be trained to maintain fire protection and life safety equipment as set out in the “Maintenance Procedures for Fire Protection” section.

All supervisory staff assigned responsibilities should complete a form similar to the one on page 13. This completed form should be kept on file, as proof of training and awareness of their assigned responsibility(ies).

Training Record – Fire Safety Responsibilities of Supervisory Staff

| Name: |  |  |
| --- | --- | --- |
| Job Title: |  |  |
| Name of Trainer: |  |  |
| Date | Description of Training | Signature |

Emergency Procedures for Occupants

Emergency procedures signage will be affixed to the wall at all fire alarm pull-stations.

In Case of Fire

Upon Discovery of Fire:

- Remain calm

- Leave fire area immediately and close doors to contain the fire.

- Sound Fire Alarm

- Call the Otonabee-South Monaghan Department of Fire and Emergency Services by calling	 9-1-1	from a safe location

(Direct lines to fire dispatch: 705-295-6811 or 705-745-3341 can be used after calling 911, if necessary.)

- Leave building via nearest Exit

- Proceed to the approved designated meeting place:

.

- Do not return to the building until advised to do so by an official from the Fire Department.

Upon Hearing Fire Alarm:

- Remain calm

- Before opening doors feel for heat

- If unsafe, stay in the room you are in with the door closed. Call 9-1-1 and be near a window to be seen from outside.

- If safe to do so, close doors behind you and leave the building via nearest exit.

- If you encounter smoke, stay low and use an alternate exit.

- Do not use the elevator

- Proceed to the approved designated meeting place:

.

- Do not return to the building until advised to do so by an official from the Fire Department.

Emergency Procedures for Supervisory Staff

Upon Discovery of Fire

- Remain calm.

- Leave fire area immediately and close doors to contain fire.  Alert occupants.

- Sound Fire Alarm and follow the fire alarm supervisory procedures.

- Call the Otonabee-South Monaghan Department of Fire and Emergency Services: 9-1-1 from a safe location. (Direct lines to Fire Dispatch: 705-295-6811 or 705-745-3341 can be used after calling 911, if necessary.).

- Exit the building via the nearest exit.

- Await the arrival of Fire Department at the main entrance and be prepared to provide an update of the situation.

Upon Hearing of a Fire Condition

- Ensure that the other occupants have been notified of the emergency conditions.

- Notify the Otonabee-South Monaghan Department of Fire and Emergency Services of the emergency condition.

- Dial 9-1-1, and ask for the Otonabee-South Monaghan Fire Department (Direct lines to Fire Dispatch: 705-295-6811 or 705-745-3341 can be used after calling 911, if necessary.).

- If it is safe to do so, supervise the evacuation of all occupants, including those       requiring assistance.

- Upon the arrival of the Fire Department, inform the Fire Officer of the conditions in the building and co-ordinate the efforts of the supervisory staff with those of the Fire Department, as requested by the Fire Department Officer(s).

- Provide access and vital information to the firefighters as to location of persons, master keys for the building and service rooms, etc.

Emergency Procedures

Additional Information/Comments

Control of Fire Hazards

(Many different types of fire hazards may be present depending on the type of occupancy. Please list ways to control the types of fire hazards which may be presented in your specific occupancy type i.e. residential, industrial, office, mercantile)

Delete any hazards which don’t apply to your occupancy and insert additional hazards, if necessary.

Here are some examples:

General Fire Hazards (not specific to occupancy type):

- Combustible materials shall not be permitted in locations or quantities that constitute a fire hazard

- Combustible materials will not be used to absorb flammable or combustible liquid spills

- Lint traps and vent ducts in laundry equipment will be cleaned regularly to prevent the accumulation of lint or obstructions.

- Ashes shall be stored in a proper safety container and not stored together with combustible materials

- Flammable liquids shall not be used for cleaning purposes

- Combustible materials shall not be stored on any roof top or in areas adjacent to the building

- Burning materials such as cigarettes or ashes should not be put into garbage bins or garbage chutes

- Shall not dispose of aerosol cans or flammable or combustible liquids in garbage bins or garbage chutes

- Practice safe cooking measures. Do not overheat any cooking utensil. Constantly attend all cooking operations. While cooking avoid clothes that contain loosely hanging sleeves and highly combustible fabrics

- Do not use unsafe electrical appliances or frayed extension cords

- Do not use extension cords as permanent wiring or over load circuitry

- Avoid careless smoking habits. Use non-combustible ashtrays. Never smoke in bed. Never smoke if feeling sleepy

- Articles such as shoes, floor mats, umbrellas, bicycles, etc… shall not be left or stored in stairwells, corridors or outside of your suite.

- Shall not wedge or prop open fire or smoke barrier doors.

- Shall ensure that all doors and door hardware operate and are maintained in accordance with the Ontario Fire Code

- Oily rags shall be disposed of in accordance to the Ontario Fire Code

- Kitchen hoods and filters shall be cleaned in accordance to the Ontario Fire Code

- Keep exits, stairways, landings and corridors and all access to exits and exits clear of obstructions and combustible materials at all times

- Keep doors to stairways closed at all times

- Ensure designated occupant loads are not exceeded.

- Supervisory staff shall participate in fire drills at intervals required by the Ontario Fire Code

- Store and use flammable and combustible liquids in quantities, locations, and containers as set out in the Ontario Fire Code.

- Report fire hazards and unsafe conditions to a Supervisory Staff member

Delete this section if you are not an Industrial Occupancy.

Control of Fire Hazards for an Industrial Occupancy:

- Some other fire hazards that may be present and that can be addressed in the Control of Fire Hazards list are as follows:

- Are aerosols used or significant quantities stored on site?

- Is industrial truck and lift equipment, battery charging operations conducted on site?

- Are combustible dusts, combustible fibers or combustible metals present or produced on site?

- Are compressed gases used or stored on site?

- Are electrical installations, temporary wiring, electrical equipment or machinery present on site that could be a potential source of ignition?

- Flammable and combustible liquids handled, stored, processed or used on site shall be done in accordance to the Ontario Fire Code?

- Is heating, ventilating and/or air conditioning equipment on site?

- Are hot works activities carried out on site, including but not limited to, cutting, welding, soldering, brazing, grinding, adhesive bonding, thermal spraying or thawing pipes?

- Are industrial trucks and lift equipment used on site, including lift trucks or forklifts, clamp trucks, tractors, sweepers and motorized hand trucks or automatic guided vehicles?

- Are oxidizing or reactive substances stored or used on site?

- Are there refueling operations taking place on site? (vehicles or machinery)

- Is smoking permitted and not controlled?

- Are substances present that would be prone to spontaneous combustion?

- Are products or materials stored or warehoused on site?

NOTE: 	Other conditions or Fire Code Requirements may apply.

e.g. Part 4 “Flammable and Combustible Liquids” in the Fire Code.

A qualified person should be obtained to ensure all requirements are met.

Delete this section if you are not an Institutional Occupancy.

Control of Fire Hazards for an Institutional Occupancy:

- Some other fire hazards that may be present and should be addressed in the “Control of Fire Hazards” list are as listed below.  List ways to control these hazards

- Smoking in institutional facilities should be closely monitored. Smoking by staff,      visitors and patients/residents should be restricted to designated areas.

- Smoking materials, such as cigarette butts and the contents of ashtrays should be disposed of with caution and never into combustible containers.

- Restrict ignition sources in areas where oxygen is in use.

- Never dispose of flammable liquids or aerosol cans in garbage chutes.

- Avoid unsafe cooking practices in kitchen areas, such as deep fat frying, loose baggy sleeves and/or unattended stoves.

- Always keep storage, laundry, furnace and electrical rooms clear of combustible materials.

- Avoid washing clothing or rags saturated with flammable or combustible liquids in laundry facilities.

- Do not store any materials or equipment in exit stairwells.

- All personal electrical appliances used by patients/residents must be closely monitored and must meet CSA Standards.

- Do not wedge open any fire doors or disengage the self-closing device installed on them.

DELETE this section if your building is not a residential property.

Residential Properties

To avoid fire hazards in the building, occupants must:

- Never put burning materials such as cigarettes and ashes into the garbage chute.

- Never dispose of flammable liquids or aerosol cans in these chutes.

- Never force cartons, coat hangers, bundles of paper into the chute because it may become blocked.

- Avoid unsafe cooking practices:  deep fat frying, too much heat, unattended stoves, loosely hanging sleeves.

- Avoid careless smoking.  Never smoke in bed.

- Never leave anything that may burn or cause a trip hazard in the halls, corridors and/or stairways.

- Always clean out clothes dryer lint collector before and after use.

- Do not use unsafe electrical appliances, frayed extension cords, over-loaded outlets or lamp wire for permanent wiring.

In general, occupants should:

- Know how to alarm occupants of building, know where exits are located.

- Call the Otonabee-South Monaghan Fire Department immediately (9-1-1, 705-745-3341 or 705-295-6811) whenever you need emergency assistance.

- Know the correct address of the building.

- Notify the building owner/property management if special assistance is required in the event of an emergency.

- Know the fire alarm signals and the procedures established to implement safe evacuation.  Read and follow the manufacturer's smoke alarm (and CO detector if   applicable) instructions, available from building owner/property management.

- Know the supervisory staff in your building.

- Report any fire hazard to supervisory staff.

- Know the stairwell designation and the crossover floors (if any).

Control of Fire Hazards

DELETE this section if your building is not a Commercial, Retail or Industrial Property.

Commercial, Retail and Industrial Properties

A high standard of housekeeping and building maintenance is probably the most important single factor in the prevention of fire.  Listed below are some specific hazards.

- Combustible material stored in non-approved areas.

- Fire and smoke barrier door not operating properly or wedged open.

- Improper storage of flammable liquids and gases.

- Defective electrical wiring and appliances, over-fusing, and the use of extension cords as permanent wiring.

- Clothes dryer lint collector full or improperly vented.

- Careless use of smoking materials.

- Kitchen hoods and filters not cleaned properly/grease laden.

- Improper disposal of oily rags.

In general, occupants should:

- Know how to alarm occupants of building, know where exits are located.

- Call the Otonabee-South Monaghan Fire Department immediately (9-1-1, 745-3341 or 295-6811) whenever you need emergency assistance.

- Know the correct address of the building.

- Notify the building/property management if special assistance is required in the event of an emergency.

- Know the fire alarm signals and the procedures established to implement safe evacuation.

- Know the supervisory staff in your building.

- Report any fire hazard to supervisory staff.

- Know stairwell designation and the crossover floors (if any).

Fire Extinguishment, Control or Confinement

In the event a small fire cannot be extinguished with the use of a portable fire            extinguisher or the smoke presents a hazard for the operator, the door to the area should be closed to confine and contain the fire.  Leave the fire area immediately via the closest exit.

Ensure that the Fire Alarm System has been activated and that the Otonabee-South Monaghan Department of Fire and Emergency Services has been notified prior to an attempt to extinguish the fire.

Only those persons who are trained and familiar with extinguisher operation may attempt to fight the fire.

Never attempt to fight a fire alone!

Suggested Operation of Portable Fire Extinguishers

Remember the acronym P.A.S.S.

P - Pull the safety pin

A - Aim the nozzle

S - Squeeze the trigger handle

S - Sweep from side to side (watch for fire restarting)

Never re-hang extinguishers after use.  Ensure they are properly recharged by a person that is qualified to service portable fire extinguishers and that a replacement extinguisher is provided.

Keep extinguishers in a visible area without obstructions around them.

The proper type of extinguisher shall be used depending on the class of fire:

| Type of Fire |  | Type of Extinguisher |
| --- | --- | --- |
| Class A | - Ordinary Combustibles - Paper, Wood, Plastics | ABC – water, multi-purpose |
| Class B | - Flammable and Combustible Liquids and Gases | BC – dry chemical ABC – multi-purpose CO2 – Carbon Dioxide Foam |
| Class C | - Live Electrical | BC – dry chemical ABC – multi-purpose CO2 – Carbon Dioxide |
| Class D | - Flammable Metals | Specialized dry chemical for the type of metal involved |
| Class K | - Cooking Oils | Class K extinguisher - |
|  | Note: Prior to using a K-type extinguisher, activate the kitchen extinguishing system to avoid electrocution. |  |

Alternative Measures for Occupant Fire Safety

In the event of a shutdown in Fire Alarm Systems, Sprinklers, or other Fire Protection Equipment or Systems, the Ontario Fire Code requires alternative measures to be provided for the safety of the occupants as per Ontario Fire Code, O.Reg. 213/07, as amended, Div. B, Subsection 2.8.2, Sentence 2.8.2.1.(2)(h).

In the event of a planned or sudden shutdown of the fire alarm system, sprinkler system, or other fire and life safety protection equipment or system, at a minimum, as dictated by Ontario Fire Code, O.Reg. 213/07, as amended, Div. B, the requirements in

- Section 6.3, Alarm and Voice Communication Systems for Life Safety; and

- Section 6.5, Sprinkler Systems,

shall be followed.

Ontario Fire Code, O.Reg. 213/07, as amended, Div. B, Section 1.1, Subsection 1.1.1., Sentence 1.1.1.1 identifies, “Where tests, repairs or alterations are made to fire protection installations, including sprinkler and stand pipe systems, a procedure of notification shall be established, and the procedure shall include notifying the fire department and the building occupants where necessary for safety in the event of a fire emergency.”

Planned or Sudden Shutdown of the Alarm Systems for Life Safety

If a fire alarm system or any part thereof is shut down, the follow is required to be competed:

- Notification – Immediately upon knowledge of the shutdown:

  - Building Occupants, by posting notices at the main entrance and all exit ways indicating the extent of the shutdown and expected duration of the shutdown.

  - Fire Department – immediately by phone 705-295-6880 (Mon.-Fri. 08:30 – 16:30) or outside of these hours: 705-745-3281 - (DO NOT USE 9-1-1 for this purpose.).

Be prepared to provide:

      - Your Name

      - Address of the building with the system shutdown

      - Description of the Problem

      - When you expect it to be repaired

      - Follow up in writing utilizing the Work Plan for a Fire Alarm System Shutdown form.

  - Supervisory Staff

  - Insurance Company

- Fire alarm systems shall be maintained in operating condition, as per the Ontario Fire Code O.Reg. 213/07, as amended, Div. B., Section 6.3, Sentence 6.3.1.4.

In the event that fire alarm system is inoperable, it shall be repaired immediately.

Work Plan for a Fire Alarm System Shutdown includes the following information:

    - Reason for Outage

    - Expected duration of the shutdown

    - Conditions for repair

    - Estimation of repair and restoration

    - Fire Safety Provisions

      - Fire Safety Patrol

      - Supervisory Responsibilities

      - Tennant Responsibilities

Planned or Sudden Shutdowns of the Sprinkler System

As per Ontario Fire Code O.Reg. 213/07, as amended, Div. B., Section 6.5.1, sentence 6.5.1.2., the sprinkler system shall be maintained in operating condition.

When any alterations, additions or repairs are to be made involving interruption to a sprinkler system or part thereof, the following items are required to be completed:

- Notification – Immediately upon knowledge of the shutdown:

  - Building Occupants, by posting notices at the main entrance and all exit ways indicating the extent of the shutdown and expected duration of the shutdown.

  - Fire Department – immediately by phone 705-295-6880 (Mon.-Fri. 08:30 – 16:30) or outside of these hours: 705-745-3281 - (DO NOT USE 9-1-1 for this purpose.).

Be prepared to provide:

      - Your Name

      - Address of the building with the system shutdown

      - Description of the Problem

      - When you expect it to be repaired

      - Follow up in writing utilizing the Work Plan for a Sprinkler System Shutdown form.

  - Supervisory Staff

  - Insurance Company

Work Plan for a Sprinkler System (secondary) shutdown includes the following information:

- Reason for Outage

- Expected duration of the shutdown

- Conditions for repair

- Estimation of repair and restoration

- Record of Fire Alarm test, post discovery of Sprinkler System Shutdown.

Assistance and direction for specific extenuating circumstances/situations may be sought from the Fire Chief or designate of the Otonabee-South Monaghan Department of Fire and Emergency Services.

The Otonabee-South Monaghan Department of Fire and Emergency Services will be notified when the work is complete and the Life Safety Systems are restored.

The building occupants will be notified when the defective system or equipment has been repaired and is operating by posting notices at the exit ways.

Planned or Sudden Shutdown of the Alarm Systems

In the event that fire alarm system is inoperable, it shall be repaired immediately.

The following work plan is in place to facilitate the repairs and will be updated as required during the shutdown/repair.

| Building Name: |  |
| --- | --- |
| Building Address: |  |
| Contact for Building: |  |
| Reason for the Outage/ Description of Problem: |  |
| Expected duration of the shutdown: |  |
| Conditions for repair: |  |
| Estimation of repair and restoration: (Timeline) |  |
| Contact for Contracted Company performing the repair: | Name: ________________________________ Phone Number: _________________________ Email: _________________________________ |

Set to Fire Department by:  Fax – 705-295-6786

Email: firechief@osmtownship.ca

Hand Delivered – 21 Third Street, Keene

Name of Person Sending: ____________________________________

Phone Number: ____________________________________________

Email: ____________________________________________________

For Fire Department Use Only:

Received by: ________________________________________

Date: _____________________		Time: _______________________

Notification Requirements

| Notification of Residents/Occupants: | Shutdown/Repair: Date: _____________ Time: _______________ Method: |
| --- | --- |
|  | Restoration: Date: _____________ Time: _______________ Method: |
| Notification of Fire Department by Phone: 705-295-6880 (Mon.-Fri. 08:30–16:30) or outside of these hours: 705-745-3281 (DO NOT USE 9-1-1 for this purpose.). | Shutdown/Repair: Date: _____________ Time: _______________ Contact person: __________________________ |
|  | Restoration: Date: _____________ Time: _______________ Contact person: __________________________ |
| Notification of Supervisory Staff: | Date: _____________ Time: _______________ Contact person: __________________________ Supervisory Responsibilities during a shut-down include: - Notifying all residents (as listed above and in the Fire Safety Plan) - Hang a door sign on all corridor suite doors to those who may require assistance escaping the building in the event of an emergency - Advising all occupants to leave the building immediately should they hear an alarm in another suite, or are advised to leave. |
| Notification of Insurance Company: | Date: _____________ Time: _______________ Contact person: __________________________ Phone Number: __________________________ |

Planned or Sudden Shutdown of the Sprinkler System

The following work plan is in place to facilitate the repairs of the sprinkler system and will be updated as required during the shutdown/repair.

| Building Name: |  |
| --- | --- |
| Building Address: |  |
| Contact for Building: |  |
| Reason for the Outage/ Description of Problem: |  |
| Expected duration of the shutdown: |  |
| Conditions for repair: |  |
| Estimation of repair and restoration: (Timeline) |  |
| Contact for Contracted Company performing the repair: | Name: ________________________________ Phone Number: _________________________ Email: _________________________________ |

Set to Fire Department by:  Fax – 705-295-6786

Email: firechief@osmtownship.ca

Hand Delivered – 21 Third Street, Keene

Name of Person Sending: ____________________________________

Phone Number: ____________________________________________

Email: ____________________________________________________

For Fire Department Use Only:

Received by: ________________________________________

Date: _____________________		Time: _______________________

Notification Requirements

| Notification of Residents/Occupants: | Shutdown/Repair: Date: _____________ Time: _______________ Method: |
| --- | --- |
|  | Restoration: Date: _____________ Time: _______________ Method: |
| Notification of Fire Department by Phone: 705-295-6880 (Mon.-Fri. 08:30–16:30) or outside of these hours: 705-745-3281 (DO NOT USE 9-1-1 for this purpose.). | Shutdown/Repair: Date: _____________ Time: _______________ Contact person: __________________________ |
|  | Restoration: Date: _____________ Time: _______________ Contact person: __________________________ |
| Notification of Supervisory Staff: | Date: _____________ Time: _______________ Contact person: __________________________ Supervisory Responsibilities during a shut-down include: - Notifying all residents (as listed above and in the Fire Safety Plan) - Hang a door sign on all corridor suite doors to those who may require assistance escaping the building in the event of an emergency - Advising all occupants to leave the building immediately should they hear an alarm in another suite, or are advised to leave. |
| Notification of Insurance Company: | Date: _____________ Time: _______________ Contact person: __________________________ Phone Number: __________________________ |

Fire Drills

The purpose of a Fire Drill is to ensure that the Occupant’s and Staff are totally familiar with the Emergency Evacuation Procedures specific to this building. This will aid in an orderly evacuation with efficient use of exit facilities in the event of a real emergency situation.

Fire Drills shall be held in conformance with the Ontario Fire Code, O. Reg. 213/07, as amended.

Fire drills will be held at least       to ensure efficient execution of the Emergency Procedures.

Fire Drill procedures shall be prepared in consultation with the Chief Fire Official (Ontario Fire Code, O. Reg. 213/07, as amended, Div. B. Sentence 2.8.3.1.(2)), and shall be included within this plan.

A Fire Drill Record (similar to the one below) shall be completed after each drill is complete.

Fire drill records are required to be retained for a period of one year.

Fire Drill Record

| Date: |  |  | Time: |  |
| --- | --- | --- | --- | --- |

| Manager/Supervisor On-Duty: |  |
| --- | --- |

| Staff Present: |  |
| --- | --- |

| Deficiencies Noted: |  |
| --- | --- |

| General Comments: |  |
| --- | --- |

Fire Drill Procedures

Maintenance Requirements

Check/Inspect/Test requirements of the Ontario Fire Code:

To assist you in fulfilling your obligations, included is a list of the portions of the Fire Code that require checks, inspections and/or tests to be conducted of the facilities.

It is suggested that you read over this list and consult with the systems specific to your building and the Ontario Fire Code to ensure that all required checks, inspections and/or tests specific to your requirements are included.

Fire Prevention Officers will check to ensure that the necessary checks, inspections and/or tests are being done, when conducting their inspections.

This list has been prepared for purposes of convenience only.  For accurate reference, the Fire Code should be consulted.

Definitions for key words are as follows:

Check	means a visual observation to ensure the device or system is in place and is not obviously damaged or obstructed.

Inspect	means a physical examination to determine that the device or system will apparently perform in accordance with its intended function.

Test	means the operation of a device or system to ensure that it will perform in accordance with its intended operation or function.

As per the requirements of the Ontario Fire Code, records of all tests and corrective measures are required to be retained for a period of two years after they are completed.

General Fire Protection Systems/Equipment

General									Responsibility

| Doors in fire separations shall be checked as frequently as necessary to ensure that they remain closed. |  |
| --- | --- |
| Exit signs shall be clearly visible and maintained in a clean and legible condition. |  |
| Internally illuminated exit signs shall be kept clearly illuminated at all times, when the building is occupied. |  |

Weekly

| When subject to accumulation of combustible deposits, hoods, filters and ducts shall be checked weekly and be cleaned when such deposits create an undue fire hazard. |  |
| --- | --- |

Monthly

| Doors in fire separations shall be inspected monthly for proper operation. |  |
| --- | --- |

Yearly

| Fire dampers and fire-stop flaps shall be inspected annually, or based on a schedule via contractor acceptable to the Chief Fire Official. |  |
| --- | --- |
| Every chimney, flue and flue pipe shall be inspected annually and cleaned as often as necessary to keep them free from accumulations of combustible deposits. |  |
| Disconnect switches for mechanical air-conditioning and ventilating systems shall be inspected annually to establish that the system can be shut down. |  |
| Spark arresters shall be cleaned annually or more frequently where accumulations of debris will adversely affect operations. Burnt-out arresters shall be repaired or replaced. |  |

### Portable Fire Extinguishers

General

(Ontario Fire Code reference Subsection 6.2.1. General)				      Responsibility

| Portable extinguishers shall be kept operable and fully charged. |  |
| --- | --- |
| Portable extinguishers shall be located so that they are easily seen and shall be accessible at all times, except as permitted. |  |

Monthly

(Ontario Fire Code reference Subsection 6.2.7. Inspection, Testing and Maintenance and in conformance with NFPA 10)		  							     Responsibility

| Portable extinguishers shall be inspected monthly. |  |
| --- | --- |
| Portable extinguishers having defects shall be repaired or recharged where necessary to ensure the extinguishers will operate effectively and safely. |  |
| Each portable extinguisher shall have a tag securely attached to it showing the maintenance or recharge date, the servicing agency and the signature of the person who performed the service. |  |
| A permanent record containing the maintenance date, the examiner’s name and a description of any work or hydrostatic testing carried out shall be prepared and maintained for each portable extinguisher. |  |
| All extinguishers shall be recharged after use or as indicated by an inspection or when performing maintenance. When recharging is performed, the recommendations of the manufacturer shall be followed. |  |

Yearly

| Extinguishers shall be subject to maintenance not more than one year apart or when specifically indicated by an inspection. |  |
| --- | --- |
| Maintenance procedures shall include a thorough examination of the three basic elements of an extinguisher: a) mechanical parts b) extinguishing agent c) expelling means |  |
| Every twelve months, pump tank water, and pump tank calcium chloride base antifreeze types of extinguishers shall be recharged with new chemicals or water, as applicable. |  |

5 Years

| Every five years, pressurized water and carbon dioxide fire extinguishers shall be hydrostatically tested. |  |
| --- | --- |

6 Years

| Every six years, stored pressure extinguishers that require a 12 year hydrostatic test shall be emptied and subjected to the applicable maintenance procedures. |  |
| --- | --- |

Fire Alarm

Not Applicable 	Applicable  - Fill out the following:

(Ontario Fire Code reference Subsection 6.3.1. General)

General									   Responsibility

| Fire alarm and voice communication system components requiring inspection shall be kept unobstructed. |  |
| --- | --- |
| Fire alarm shall be kept unobstructed. |  |
| Fire alarm and voice communication systems shall be maintained in operating condition. |  |
| Disconnect switches for power supplies which serve only fire alarm systems or interconnected smoke alarms shall be in a locked secure area or otherwise secured in an approved manner. |  |

Daily

(Ontario Fire Code reference Subsection 6.3.2. Check, Inspect and Test)

| The following daily checks shall be conducted if a fault is established, appropriate corrective action shall be taken. a) Check the principle and remote trouble lights for trouble indication; b) Inspection of the AC power-on light shall be done to ensure its normal operation. |  |
| --- | --- |

Monthly

| Every month the following tests shall be conducted under battery back up power and if a fault is established, appropriate corrective action shall be taken: a) one manual fire alarm initiating device shall be operated, on a rotating basis, and shall initiate an alarm condition b) function of all signal devices shall be ensured c) the annunciator panel shall be checked to ensure correct annunciation d) intended function of the audible and visual trouble signals shall be ensured e) fire alarm batteries shall be checked to ensure that: i) terminals are clean and lubricated where necessary; ii) terminal clamps are clean and tight; - electrolyte level and specific gravity, where applicable, meet manufacturer’s specifications |  |
| --- | --- |

Monthly (continued)							Responsibility

| Voice paging capability to one zone shall be tested monthly on a rotational basis. |  |
| --- | --- |
| One emergency telephone shall be tested monthly on a rotational basis for operation and correct indication at control unit. |  |
| Loudspeakers shall be tested monthly as an all-call signal to ensure they function as intended. |  |
| At least one firefighter’s emergency telephone shall be tested monthly on a rotational basis to ensure communication with the control unit. All telephones shall be tested each year. |  |

Yearly

| Yearly tests conducted by a certified alarm contractor as required by The Ontario Fire Code, Section 1.1.5.3. Tests shall be in conformance with CAN/ULC S536, “Inspection and Testing of Fire Alarm Systems”. |  |
| --- | --- |
| Voice communications between floor areas and the central alarm control facility shall be tested annually, as required for fire alarm initiating and signally devices. |  |

Smoke Alarms

Not Applicable 	Applicable  - Fill out the following:

General									Responsibility

| Ensure dwelling unit smoke alarms are maintained in operating condition. |  |
| --- | --- |
| Ensure a copy of the smoke alarm manufacturer’s Maintenance instructions or approved alternative has been provided. |  |

Standpipe Systems

Not Applicable 	Applicable  - Fill out the following:

(Ontario Fire Code reference Subsection 6.4.2. Maintenance and Inspection of Hose Stations and Equipment and Ontario Fire Code reference Subsection 6.4.3. Testing)

Monthly									Responsibility

| Hose cabinets shall be inspected monthly to ensure that the hose and equipment are in the proper position and appear to be in operable condition. |  |
| --- | --- |
| Standpipe hose stations shall be conspicuously identified and unobstructed. |  |

Yearly

| Hose valves shall be inspected annually to ensure that they are tight so that there is no water leakage into the hose. |  |
| --- | --- |
| Standpipe hose shall be inspected and replaces on the rack annually and after each use, and any worn hose or gaskets in the couplings at the hose valve and the nozzle replaced. |  |
| Plugs or caps on Fire Department connections shall be removed annually and the threads inspected for wear, rust or obstruction. Re-secure plugs or caps, wrench tight. |  |
| If plugs or caps are missing, examine the Fire Department connections for obstructions, back flush if necessary, and replace plugs or caps. |  |

Sprinkler Systems (Wet)

Not Applicable 	Applicable  - Fill out the following:

General									Responsibility

| Auxiliary drains shall be inspected as required to prevent freezing. |  |
| --- | --- |

Weekly

| Except for electrically supervised valves, all valves controlling water supplies to sprinklers and alarm connections shall be checked weekly to ensure that they are sealed or locked in the open position. |  |
| --- | --- |
| Water supply pressure and system air or water pressure shall be checked weekly by using gauges to ensure that the system is maintained at the required operating pressure. |  |

Monthly

| On all sprinkler systems, an alarm test, using the alarm test connection located at the sprinkler valve, shall be performed monthly. |  |
| --- | --- |

Two Months

| All transmitters and water flow devices shall be tested at two month intervals. |  |
| --- | --- |

Six Months

| Gate-valve supervisory switches and other sprinkler system supervisory devices shall be tested at six month intervals. |  |
| --- | --- |

Yearly									Responsibility

| Exposed sprinkler piping hangers shall be checked yearly to ensure that they are kept in good repair. |  |
| --- | --- |
| Sprinkler heads shall be checked at least once per year to ensure that they are kept in good repair. |  |
| Sprinkler heads shall be checked at least once per year to ensure that they are free from damage, corrosion, grease, dust, paint, or whitewash. They shall be replaced where necessary as a result of such conditions. |  |
| On wet sprinkler systems, water-flow alarm test using the most hydraulically remote test connection, shall be performed annually. |  |
| Sprinkler system water pressure shall be tested annually or after any sprinkler system control valve has been operated, with the main drain valve fully open, to ensure that there are no obstructions or deterioration of the main water supply. |  |
| Plugs or caps on Fire Department connections shall be removed annually and the threads inspected of wear, rust or obstruction. Re-secure plugs or caps, wrench tight. If plugs or caps are missing, examine the Fire Department connection for obstructions, back flush if necessary and replace plugs or caps. |  |

Sprinkler Systems (Dry)

Not Applicable 	applicable  - Fill out the following:

General									   Responsibility

| Auxiliary drains shall be inspected as required to prevent freezing. |  |
| --- | --- |
| Dry-pipe valve rooms or enclosures in unheated buildings shall be checked as often as necessary when the outside temperature falls below 0o Celsius to ensure that the system does not freeze. |  |

Weekly

| Except for electrically supervised valves, all valves controlling water supplies to sprinklers and alarm connections shall be checked weekly to ensure that they are sealed or locked in the open position. |  |
| --- | --- |
| Water supply pressure and system air or water pressure shall be checked weekly by using gauges to ensure that the system is maintained at the required operating pressure. |  |
| System pressure gauges shall be checked weekly. The system shall be maintained at the required operating pressure. |  |

Monthly

| On all sprinkler systems, an alarm test, using the alarm test Connection located at the sprinkler valve, shall be performed monthly. |  |
| --- | --- |

2 Months

| All transmitters and water flow devices shall be tested at two month intervals. |  |
| --- | --- |

3 Months

| The priming water supply for dry pipe systems shall be inspected every three months to ensure that the proper level above the dry pipe valve is maintained. |  |
| --- | --- |

6 Months

| Gate-valve supervisory switches and other sprinkler system supervisory devices shall be tested at six month intervals. |  |
| --- | --- |

Sprinkler Systems (Dry) – con’t

Yearly

| Exposed sprinkler piping hangers shall be checked yearly to ensure that they are kept in good repair. |  |
| --- | --- |
| Sprinkler heads shall be checked at least once per year to ensure that they are free from damage, corrosion, grease dust, paint, or whitewash. They shall be replaced where necessary as a result of such conditions. |  |
| Sprinkler system water pressure shall be tested annually or after any sprinkler system control valve has been operated, with the main drain valve fully open, to ensure that there are no obstructions or deterioration of the main water supply. |  |
| Plugs or caps on Fire Department connections shall be removed annually and the threads inspected for wear, rust or obstruction. Re-secure plugs or caps wrench tight. If plugs or caps are missing, examine the Fire Department connection for obstructions, back flush if necessary and replace plugs or caps. |  |
| Dry pipe valves shall be tripped annually by means of the system test pipe, to ensure that they operate satisfactorily and that the sprinkler alarms are in operating condition. A full flow trip test, with the control valve fully open, shall be conducted at least every three years. |  |

15 Years

| Every fifteen years, dry pipe systems shall be inspected for obstructions in the sprinkler piping and if necessary, the entire system shall be flushed of foreign material. |  |
| --- | --- |

Water Supplies for Firefighting (Fire Pumps)

Not Applicable 	Applicable  - Fill out the following

Daily										  Responsibility

| The temperature of pump rooms shall be checked daily during freezing weather. |  |
| --- | --- |

Weekly

| Valves controlling water supplies exclusively for fire protection systems shall be inspected weekly to ensure that they are fully open and sealed or locked in that position. |  |
| --- | --- |
| Fire pumps shall be started once per week at rated speed. The fire pump discharge pressure, suction pressure, lubricating oil level, operative condition of relief valves, priming water level and general operating conditions shall be inspected. |  |
| Internal combustion engine fire pumps shall be operated once per week for a sufficient time to bring the engine up to normal operating temperature. The storage batteries, lubrication systems and fuel supplies shall be inspected. |  |

Yearly

| Fire pumps shall be tested annually at full rated capacity to ensure that they are capable of delivering the rated flow. |  |
| --- | --- |

Private Fire Hydrants

Not Applicable 	Applicable  - Fill out the following

General									Responsibility

| Hydrants shall be readily available and unobstructed for use at all times. |  |
| --- | --- |

Yearly

| Hydrants shall be inspected annually after each use. |  |
| --- | --- |
| Ensure hydrants are equipped with port caps secured wrench tight. The port caps shall be removed annually and inspected for wear, rust or obstructions. |  |
| The hydrant barrel shall be inspected annually to ensure that no water has accumulated. |  |
| The drain valve shall be inspected for operation if water is found in the hydrant barrel when main valve is closed. |  |
| Hydrant water flow shall be inspected annually and a record shall be kept. |  |

Water Supplies for Firefighting (Water Tanks)

Not Applicable 	Applicable  - Fill out the following

Daily										Responsibility

| Water tank heat equipment, tank enclosure and/or water temperature shall be checked daily during freezing weather. |  |
| --- | --- |

Weekly

| Water levels and air pressure in pressure tanks shall be checked weekly and the relief valves on the air and the water lines shall be inspected weekly. |  |
| --- | --- |

Monthly

| Water level in gravity tanks shall be inspected monthly. |  |
| --- | --- |

Yearly

| An annual inspection shall be made of water tanks for fire protection, tank supporting structures and water supply systems including piping, control valves, check valves, heating systems, mercury gauges and expansion joints to ensure that they are in operating condition. |  |
| --- | --- |
| Cathodic protection equipment in water tanks shall be inspected annually. |  |

2 Years

| Water tanks shall be checked every two years for corrosion. |  |
| --- | --- |

5 Years

| Water tanks shall be inspected every five years and scraped and repainted as required. |  |
| --- | --- |

Smoke Shafts and Venting Equipment

Not Applicable 	Applicable  - Fill out the following

General									Responsibility

| Access to windows and panels required for venting floor areas and vents to vestibules permitted to be manually openable shall be kept free of obstructions, openable without keys and operable at times. |  |
| --- | --- |

6 Months

| All elevators in an elevator shaft, that is intended for use as a smoke shaft, be inspected semi-annually to ensure that on activation of the fire alarm system, the elevators will return to the street floor and remain inoperative. |  |
| --- | --- |

Yearly

| A closure in an opening to the outdoors at the top of a smoke shaft, shall be inspected annually to ensure that it will open: a) manually, outside from the building b) on a signal from the smoke/heat actuated device in the smoke shaft, and; c) when a closure in an opening between a floor area and the smoke shaft opens |  |
| --- | --- |
| Controls for air-handling systems for venting in the event of a fire, shall be inspected annually to ensure that air is exhausted from each floor area to the outdoors. |  |

5 Years

| Closures in vent openings into smoke shafts from each floor shall be inspected sequentially over a period not to exceed 5 years. |  |
| --- | --- |

Smoke Control Measures

Not Applicable 		Applicable  - Fill out the following:

General 									     Responsibility

| Where smoke control measures contained in the supplement to the National Building Code of Canada 1995, Chapter 3, “Measures for Fire Safety in High Buildings” are used, the inspections and tests shall be as outlined in Section 7.3 of the National Fire Code of Canada. |  |
| --- | --- |
| Where a smoke control system is designed to meet the requirements of The Ontario Building Code, the inspections and tests shall be in accordance with procedures established by the designer of the system. |  |

Commercial Cooking Equipment

Not Applicable 		Applicable  - Fill out the following:

General									Responsibility

| Commercial cooking equipment exhaust and fire protection systems shall be installed and maintained in conformance with NFPA 96, “Ventilation Control and Fire Protection of Commercial Cooking Operations”. |  |
| --- | --- |
| Ensure wet chemical or alkali based dry chemical portable fire extinguishers are provided to protect commercial cooking equipment and are readily available for use in an emergency. |  |

Weekly

| Hoods, grease removal devices, fans, ducts, and other equipment shall be checked weekly and cleaned at frequent intervals, prior to surfaces becoming heavily contaminated with grease or oily sludge. |  |
| --- | --- |

6 Months

| Inspection and servicing of the fire extinguishing system shall be made at least every six months by properly trained and qualified persons in conformance with Ontario Fire Code, Section 6.8.1.1. |  |
| --- | --- |

Emergency Lighting System

Not Applicable 	Applicable  - Fill out the following:

Daily										  Responsibility

| Check pilot lights for indication of proper operation. |  |
| --- | --- |

Monthly

| Batteries shall be inspected monthly and maintained as per manufacturer’s specifications. |  |
| --- | --- |
| Ensure that battery surface is clean and dry. |  |
| Ensure that terminal connections are clean, free of corrosion and lubricated. |  |
| Ensure that the terminal clamps are clean and tight as per manufacturer’s specifications. |  |
| Emergency lighting equipment shall be tested monthly to ensure that the emergency lighting will function upon failure of the primary power supply. |  |

Yearly

| Emergency lighting equipment shall be tested annually to ensure that the units will provide emergency lighting for a duration equal to the design criteria under simulated power failure conditions. |  |
| --- | --- |
| After completion, the charging conditions for voltage and current and the recovery period will be tested annually to ensure that the charging system is in accordance with the manufacturer’s specifications. |  |

Emergency Power Systems

Not Applicable 	Applicable  - Fill out the following:

General									Responsibility

| Emergency power systems shall be inspected, tested and maintained in conformance with CSA C282, “Emergency Electrical Power Supply for Buildings”. |  |
| --- | --- |
| To ensure continued reliable operation, the emergency power supply equipment shall be operated and maintained in accordance with manufacturer’s instructions. |  |
| At least two copies of the instruction manual shall be maintained. |  |

Monthly

| The emergency electrical power shall be completely tested monthly as follows: a) Simulate a failure of the normal power supply. b) Arrange so that: i) an engine generator set operates under at least 30% of the rated load for 60 minutes and; ii) all automatic transfer switches are operated under load. c) Include an inspection for correct function of all auxiliary equipment such as radiator shutter control, coolant pumps, fuel transfer pumps, oil coolers and engine room ventilation controls. d) Record all instrument readings associated with the prime mover and generator and a verification that they are normal. e) Log and report as further prescribed in the manual of instruction for operation and maintenance. - Check fuel supply for sufficient quantity. |  |
| --- | --- |

Annually

| Test the generator, control panel, and transfer switch in conformance with CSA C282, “Emergency Electrical Power Supply for Buildings”. |  |
| --- | --- |

Maintenance

Additional Comments

Building Schematics

Legend for Building/Unit Fire Emergency System

|  | Pull Pin For Kitchen Fire Suppression System |
| --- | --- |
|  | Entrance / Exit |
|  | Hydrant |
|  | Siamese Fire Department Connection |
|  | Free Standing Siamese Fire Department Connection |
|  | Valves (General) Identify The Type Of Valve (Ie. Shut Off Valve For Natural Gas, Sprinklers, Etc.) |
|  | Fire Alarm Control Panel |
|  | Fire Alarm Annunciator |
|  | Emergency Light, Battery-Powered |
|  | Illuminated Exit Sign, Single Face |
|  | Combined Battery-Powered Emergency Light & Illuminated Exit Sign |
|  | Pull Station |
|  | Heat Detector |
|  | Smoke Detector |
|  | Fire Extinguisher - BC Type |
|  | Fire Extinguisher - ABC Type |
|  | Fire Extinguisher - Water |
| H | Hose Cabinet |
|  | Sprinkler Riser, indicate whether Wet or Dry System |

Site Plan

(Include Legend)

Please attach to e-mail, use postal mail (address is on the final page of this document), or fax to 705-295-6786.

Please indicate your company name so the plan can be attached to your submission.

Floor/Area Plan

Title:

Business:

(Include Legend)

Please attach to e-mail, use postal mail (address is on the final page of this document), or fax to 705-295-6786.

Please indicate your company name so the plan can be attached to your submission.

Floor/Area Plan

Title:

Business:

(Include Legend)

Please attach to e-mail, use postal mail (address is on the final page of this document), or fax to 705-295-6786.

Please indicate your company name so the plan can be attached to your submission.

Floor/Area Plan

Title:

Business:

(Include Legend)

Please attach to e-mail, use postal mail (address is on the final page of this document), or fax to 705-295-6786.

Please indicate your company name so the plan can be attached to your submission.

Floor/Area Plan

Title:

Business:

(Include Legend)

Please attach to e-mail, use postal mail (address is on the final page of this document), or fax to 705-295-6786.

Please indicate your company name so the plan can be attached to your submission.

Floor/Area Plan

Title:

Business:

(Include Legend)

Please attach to e-mail, use postal mail (address is on the final page of this document), or fax to 705-295-6786.

Please indicate your company name so the plan can be attached to your submission.

Floor/Area Plan

Title:

Business:

(Include Legend)

Please attach to e-mail, use postal mail (address is on the final page of this document), or fax to 705-295-6786.

Please indicate your company name so the plan can be attached to your submission.

Chief Fire Official

Otonabee-South Monaghan

Department of Fire & Emergency Services

21 Third Street; P.O. Box 70

Keene, ON   K0L 2G0

firechief@osmtownship.ca